## DAPR Projects 5yr view (2025)
Field Name | Rule | Data Type | Units | Other information
Project ID |  | Text |  | Project number | NPR-000070 | NPR-000069 | NPR-000049 | NPR-000533 | NPR-000053 | NPR-000052 | NPR-000054 | NTM-000535
Asset Name |  | Text |  | Substation or feeder name(s) | Box Hill ZS | West Appin ZS | Mt Gilead ZS | 132kV Cable Constraints in the Parramatta area | Austral ZS | Cambewarra ZS | Catherine Park ZS | Replacement of end of life 132kV oil filled cables in the Parramatta area
Constraint primary driver | DT001 | Text |  | Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Reliability & Safety & Environment
Location of constraint (start) | DT002 | Decimal | Lattitude° ,Longitude° |  | -33.637224, 150.898978 | −34.20356, 150.77143 | -34.139089, 150.769423 | -33.824824, 151.030938 | -33.931801, 150.817902 | -34.857960, 150.597903 | −34.00857, 150.75702 | -33.824824, 151.030938
Location of constraint (end) | DT003 | Decimal | Lattitude° ,Longitude° |  | -33.637224, 150.898978 | −34.20356, 150.77143 | -34.139089, 150.769423 | -33.824824, 151.030938 | -33.931801, 150.817902 | -34.857960, 150.597903 | −34.00857, 150.75702" | -33.824824, 151.030938
Asset ID | DT004 | Text |  | Consistent with RIN Sustained Interruptions sheet from Category Analysis template | NPR-000070 Augmentation of Box Hill ZS | NPR-000069 Establishment of West Appin ZS | NPR-000049 Establishment of Mt Gilead ZS | NPR-000533 132kV Cable Constraints in the Parramatta area | NPR-000053 Austral ZS | NPR-000052 Cambewarra Capacity Increase | NPR-000054 Capacity Increase for the Catherine Fields Growth Areas | Replacement of end of life 132kV oil filled cables in the Parramatta area
Network Element | DT005 | Text |  | Choose one of: Transmission connection point; zone substation; sub-transmission line; feeder | Zone Substation | Zone Substation | Zone Substation | Sub-transmission Line | Zone Substation | Zone Substation | Zone Substation | Sub-transmission Line
Residential customers affected | DT006 | Integer | Total number of customers affected |  | >1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000
Residential customers affected | DT006_a | Decimal | % of total customers affected |  | NA | NA | NA | NA | NA | NA | NA | NA
Voltage level | DT009 | Decimal | KV | Highest operational voltage level of the assets involved in the constraints | 132 | 66 | 66 | 132 | 132 | 11 | 132 | 132
Preferred network investment | DT012 | Text |  | Brief description: Free text | Augment existing ZS | New ZS within the West Appin area | New ZS within the Gilead Precinct | Augmenting 132kV supply to Parramatta | Establish new ZS | Establish new 11kV Feeder | Establish new ZS | Replace cables at end of life with modern equivalent of increased capacity
Preferred network investment capital cost | DT013 | Decimal | $ (real) |  | 51356893 | 33509595 | 35000000 | 4319281 | 23400000 | 9713000 | 36600000 | 41800000
Preferred annual network investment operating cost | DT013_a | Decimal | $ (real) | Annual operating costs (including overheads, risk allowance and contingency allowance if included) | 205427.572 | 134038.38 | 140000 | 17277.124 | 93600 | 38852 | 146400 | 167200
Preferred network investment cost accuracy | DT014_a | Decimal | +% |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Preferred network investment cost accuracy | DT014_b | Decimal | -% |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Proposed timing FNY | DT015 | Date | MM/YYYY |  | FY28 | FY29 | FY31 | FY29 | FY30 | FY31 | FY29 | FY29
Demand reduction required to defer investment by 1 year | DT016 | Decimal | MVA | MVA | 6.8915 | 80.8421 | 15.7895 | 2.85 | 49.1579 | 17.4716 | 4.4 | N/A
Demand reduction required to defer investment by 1 year | DT016_a | Decimal | MW | If MW data is collected | 6.5469 | 76.8 | 15 | 2.7075 | 46.7 | 16.598 | 4.18 | N/A
Annual Deferral Value | DT017 | Decimal | $ (real) | Using an appropriate VCR as an input | 1679370.4011 | 971480 | 1386807 | 141240.4887 | 765180 | 317615.1 | 1196820 | 1366860
Load transfer capability | DT017 | Decimal | MVA | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load transfer capability | DT017_a | Decimal | MW | If MW data is collected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation | DT018 | Decimal | MVA | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation | DT018_a | Decimal | MW | If MW data is collected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Historic use of existing emergency response | DT019 | Series | DD/MM/YYYY HH:MM; MVA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic use of existing emergency response | DT019_a | Series | DD/MM/YYYY HH:MM; MW | If MW data is collected | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating | DT021 | Series | HH:MM DD/MM/YYYY MVA; | 3 years historic, 30 minute intervals uncleansed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating | DT021_a | Series | HH:MM DD/MM/YYYY MW; | 3 years historic; 30 minute intervals, uncleansed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Forecast Load Energy at Risk_25
| Project ID | NPR-000070 | NPR-000069 | NPR-000049 | NPR-000533 | NPR-000053 | NPR-000052 | NPR-000054 | NTM-000535
| Asset Name | Box Hill ZS | West Appin ZS | Mt Gilead ZS | 132kV Cable Constraints in the Parramatta area | Austral ZS | Cambewarra ZS | Catherine Park ZS | Replacement of end of life 132kV oil filled cables in the Parramatta area
| Asset ID | NPR-000070 Augmentation of Box Hill ZS | NPR-000069 Establishment of West Appin ZS | NPR-000049 Establishment of Mt Gilead ZS | NPR-000533 132kV Cable Constraints in the Parramatta area | NPR-000053 Austral ZS | NPR-000052 Cambewarra Capacity Increase | NPR-000054 Capacity Increase for the Catherine Fields Growth Areas | Replacement of end of life 132kV oil filled cables in the Parramatta area
Asset Rating (MVA firm) | Year
| 2026 | 22.2 | 5.17 | 3.27 | 93 | 50 | 2.39 | 15.9 | 0
| 2027 | 18.2 | 5.17 | 4.57 | 93 | 50 | 2.38 | 15.9 | 0
| 2028 | 18.2 | 5.17 | 6.51 | 93 | 50 | 2.37 | 15.9 | 0
| 2029 | 18.2 | 5.17 | 8.46 | 93 | 50 | 2.35 | 15.9 | 0
| 2030 | 18.2 | 5.17 | 11.04 | 93 | 50 | 2.34 | 15.9 | 0
Asset Rating (MW firm) Formula, assuming a PF | Year
| 2026 | 21.09 | 4.9115 | 7.94 | 88.35 | 47.5 | 2.2705 | 15.105 | 0
| 2027 | 17.29 | 4.9115 | 7.94 | 88.35 | 47.5 | 2.261 | 15.105 | 0
| 2028 | 17.29 | 4.9115 | 7.94 | 88.35 | 47.5 | 2.2515 | 15.105 | 0
| 2029 | 17.29 | 4.9115 | 7.94 | 88.35 | 47.5 | 2.2325 | 15.105 | 0
| 2030 | 17.29 | 4.9115 | 7.94 | 88.35 | 47.5 | 2.223 | 15.105 | 0
Forecast Demand 50% POE (MVA) | Year
| 2026 | 30.495 | 5.7 | 3.27 | 121 | 67.8 | 2.93 | 17 | 0
| 2027 | 36.4736 | 6.19 | 4.57 | 134 | 76.2 | 3.42 | 18.6 | 0
| 2028 | 43.7278 | 7.86 | 6.51 | 145 | 82.2 | 4.07 | 19.9 | 0
| 2029 | 48.3813 | 10.14 | 8.46 | 148 | 85.9 | 4.72 | 20.3 | 0
| 2030 | 53.0347 | 15.79 | 11.04 | 152 | 88 | 5.38 | 20.7 | 0
Forecast Demand 50% POE (MW) Formula, assuming a PF | Year
| 2026 | 28.9703 | 5.415 | 3.1065 | 114.95 | 64.41 | 2.7835 | 16.15 | 0
| 2027 | 34.65 | 5.8805 | 4.3415 | 127.3 | 72.39 | 3.249 | 17.67 | 0
| 2028 | 41.5414 | 7.467 | 6.1845 | 137.75 | 78.09 | 3.8665 | 18.905 | 0
| 2029 | 45.9622 | 9.633 | 8.037 | 140.6 | 81.605 | 4.484 | 19.285 | 0
| 2030 | 50.383 | 15.0005 | 10.488 | 144.4 | 83.6 | 5.111 | 19.665 | 0
Forecast Demand 10% POE (MVA) | Year
| 2026 | 30.495 | 5.7 | 3.27 | 121 | 74.58 | 2.93 | 18.7 | 0
| 2027 | 36.4736 | 6.19 | 4.57 | 134 | 83.82 | 3.42 | 20.46 | 0
| 2028 | 43.7278 | 7.86 | 6.51 | 145 | 90.42 | 4.07 | 21.89 | 0
| 2029 | 48.3813 | 10.14 | 8.46 | 148 | 94.49 | 4.72 | 22.33 | 0
| 2030 | 53.0347 | 15.79 | 11.04 | 152 | 96.8 | 5.38 | 22.77 | 0
Forecast Demand 10% POE (MW) Formula | Year
| 2026 | 28.9703 | 5.415 | 3.1065 | 114.95 | 70.851 | 2.7835 | 17.765 | 0
| 2027 | 34.65 | 5.8805 | 4.3415 | 127.3 | 79.629 | 3.249 | 19.437 | 0
| 2028 | 41.5414 | 7.467 | 6.1845 | 137.75 | 85.899 | 3.8665 | 20.7955 | 0
| 2029 | 45.9622 | 9.633 | 8.037 | 140.6 | 89.7655 | 4.484 | 21.2135 | 0
| 2030 | 50.383 | 15.0005 | 10.488 | 144.4 | 91.96 | 5.111 | 21.6315 | 0
Maximum Load at risk (MW) Formula | Year
| 2026 | 7.8803 | 0.5035 | 0 | 26.6 | 16.91 | 0.513 | 1.045 | 0
| 2027 | 17.36 | 0.969 | 0 | 38.95 | 24.89 | 0.988 | 2.565 | 0
| 2028 | 24.2514 | 2.5555 | 0 | 49.4 | 30.59 | 1.615 | 3.8 | 0
| 2029 | 28.6722 | 4.7215 | 0.097 | 52.25 | 34.105 | 2.2515 | 4.18 | 0
| 2030 | 33.093 | 10.089 | 2.548 | 56.05 | 36.1 | 2.888 | 4.56 | 0
Expected Unserved Energy (MWh) | Year
| 2026 | 0 | 2.6 | 0 | 1.4 | 0.6 | 0.068 | 0.48 | 0
| 2027 | 0.00073412 | 6.3 | 0 | 6.2 | 3.1 | 0.337 | 12.71 | 0
| 2028 | 0.26938 | 12.3 | 0 | 42.6 | 8.8 | 1.394 | 28.46 | 0
| 2029 | 12.678 | 89.1 | 0 | 74.6 | 35.5 | 3.957 | 34 | 0
| 2030 | 101.6584 | 200.2 | 15 | 699.3 | 82.2 | 20.555 | 35.39 | 0