## DAPR Projects 5yr view
Field Name | Rule | Data Type | Units | Other information
Project ID |  | Text |  | Project number | NPR-000771 | NPR-000044 | NPR-000013 | NPR-000805 | NPR-000008 | NPR-000451 | NPR-000060 | NPR-000067 | NPR-000053 | NPR-000070 | NPR-000061 | NPR-000048 | NTM-000009 | NPR-000533 | NPR-000052 | NPR-000049 | NPR-000068
Asset Name |  | Text |  | Substation or feeder name(s) | Third Transformer Eastern Creek ZS | Lowes Creek ZS | West Dapto ZS | North Kemps Creek ZS | Culburra Beach ZS | East Parramatta ZS | Permanent Berrima Junction ZS | Northern Gateway ZS | Austral ZS | Box Hill ZS | Menangle Park ZS | East Riverstone ZS | 132kV Oil Cable Replacement | 132kV Cable Constraints | Cambewarra TS ZS | Mt Gilead ZS | Agribusiness North ZS
Constraint primary driver | DT001 | Text |  | Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Reliability & Safety & Environment | Capacity | Capacity | Capacity | Capacity
Location of constraint (start) | DT002 | Decimal | Lattitude° ,Longitude° |  | -33.812302, 150.833287 | - 33°58'47.80", 150°44'6.35" | -34.479672, 150.773286 | -33.856897, 150.790672 | -34.932050, 150.743661 | -33.814734, 150.995349 | - 34°31'13.40, 150°21'57 | -33.8627648,150.7213597 | -33.894212, 150.818994 | -33.637224, 150.898978 | -34.093151, 150.751829 | -33.663998, 150.893481 | -33.824824, 151.030938 | -33.824824, 151.030938 | -34.827831, 150.568554 | -34.139089, 150.769423 | -33.892822, 150.694797
Location of constraint (end) | DT003 | Decimal | Lattitude° ,Longitude° |  | -33.812302, 150.833287 | - 33°58'47.80", 150°44'6.35" | -34.479672, 150.773286 | -33.856897, 150.790672 | -34.932050, 150.743661 | -33.814734, 150.995349 | - 34°31'13.40, 150°21'57 | -33.8627648,150.7213597 | -33.894212, 150.818994 | -33.637224, 150.898978 | -34.093151, 150.751829 | -33.663998, 150.893481 | -33.824824, 151.030938 | -33.824824, 151.030938 | -34.827831, 150.568554 | -34.139089, 150.769423 | -33.892822, 150.694797
Asset ID | DT004 | Text |  | Consistent with RIN Sustained Interruptions sheet from Category Analysis template | NPR-000771 Augmentation Eastern Creek ZS 3rd Transformer | NPR-000044 Lowes Creek ZS Establishment | NPR-000013 - Establishment of West Dapto ZS | NPR-000805 Establishment of North Kemps Creek ZS | NPR-000008 - Establishment of Culburra Beach ZS | NPR-000451 Augmentation of East Parramatta ZS | NPR-000060 - Permanent Berrima Junction ZS | NPR-000067 Establishment of Northern Gateway ZS | NPR-000053 Establishment of Austral ZS | NPR-000070 Augmentation of Box Hill ZS | NPR-000061 Augmentation of Menangle Park ZS | NPR-000048 Establishment of East Riverstone ZS | Replacement of end of life 132kV oil filled cables in the Parramatta area | 132kV Cable Constaints in the Parramatta area. Augmenting 132kV supply to Parramatta | NPR-000052 Establishment of Cambewarra TS ZS | NPR-000049 Establishment of Mt Gilead ZS | NPR-000068 Establishment of Agribusiness North ZS
Network Element | DT005 | Text |  | Choose one of: Transmission connection point; zone substation; sub-transmission line; feeder | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Sub-transmission Line | Sub-transmission Line | Zone Substation | Zone Substation | Zone Substation
Residential customers affected | DT006 | Integer | Total number of customers affected |  | <1000 | <1000 | >1000 | <1000 | >1000 | >1000 | <1000 | <1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000 | <1000
Residential customers affected | DT006_a | Decimal | % of total customers affected |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Voltage level | DT009 | Decimal | KV | Highest operational voltage level of the assets involved in the constraints | 132 | 132 | 33 | 132 | 33 | 132 | 33 | 132 | 33 | 132 | 66 | 33 | 132 | 132 | 33 | 66 | 132
Preferred network investment | DT012 | Text |  | Brief description: Free text | Install additional transformer. | Establish new ZS | Establish new ZS | Establish new ZS | Establish new ZS | Convert East Parramatta Switching Station to a firm 45MVA Zone Substation | Augment temporary zone substation into a permanent firm substation to supply employment lands | Establish new ZS | Establish new ZS | Augment Box Hill ZS to a firm 45MVA Zone Substation and establish subtransmission feeder to Mungerie Park ZS. | New ZS within Menangle Park | New ZS at East Riverstone | Replace cables at end of life with modern equivalent of increased capacity | Install dynamic reactance devices on feeders 22U and 9J8. | Mobile 132/11kV Zone Substation | New ZS within the Gilead Precinct | Establish new ZS
Preferred network investment capital cost | DT013 | Decimal | $ (real) |  | 3600000 | 22478000 | 23600000 | 21000000 | 19423953 | 12200000 | 16400000 | 31100000 | 21400000 | 12600000 | 18793000 | 25500000 | 46200000 | 1900000 | 4608900 | 16540000 | 18000000
Preferred annual network investment operating cost | DT013_a | Decimal | $ (real) | Annual operating costs (including overheads, risk allowance and contingency allowance if included) | 14400 | 89912 | 94400 | 84000 | 77695.812 | 48800 | 65600 | 124400 | 85600 | 50400 | 75172 | 102000 | 184800 | 7600 | 18435.6 | 66160 | 72000
Preferred network investment cost accuracy | DT014_a | Decimal | +% |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Preferred network investment cost accuracy | DT014_b | Decimal | -% |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Proposed timing FNY | DT015 | Date | MM/YYYY |  | FY26 | FY27 | FY29 | FY27 | FY29 | FY28 | FY27 | FY26 | FY27 | FY29 | FY28 | FY28 | FY28 | FY28 | FY29 | FY28 | FY28
Demand reduction required to defer investment by 1 year | DT016 | Decimal | MVA | MVA | 15 | 5 | 5 | 8 | 1 | 7 | 9 | 9 | 10 | 5 | 5 | 16 | N/A | 15 | 5 | 5 | 5
Demand reduction required to defer investment by 1 year | DT016_a | Decimal | MW | If MW data is collected | 15 | 5 | 5 | 8 | 1 | 7 | 8.55 | 9 | 10 | 5 | 5 | 16 | N/A | 15 | 5 | 5 | 5
Annual Deferral Value | DT017 | Decimal | $ (real) | Using an appropriate VCR as an input | 117360 | 732782.8 | 769360 | 684600 | 633220.8678 | 397720 | 534640 | 1013860 | 697640 | 410760 | 612651.8 | 831300 | 1506120 | 61940 | 150250.14 | 539204 | 586800
Load transfer capability | DT017 | Decimal | MVA | MVA | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load transfer capability | DT017_a | Decimal | MW | If MW data is collected | 0 | 0 | 0 | 0 | 1.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation | DT018 | Decimal | MVA | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation | DT018_a | Decimal | MW | If MW data is collected | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Historic use of existing emergency response | DT019 | Series | DD/MM/YYYY HH:MM; MVA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic use of existing emergency response | DT019_a | Series | DD/MM/YYYY HH:MM; MW | If MW data is collected | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating | DT021 | Series | HH:MM DD/MM/YYYY MVA; | 3 years historic, 30 minute intervals uncleansed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating | DT021_a | Series | HH:MM DD/MM/YYYY MW; | 3 years historic; 30 minute intervals, uncleansed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Note on F9: Matthew Brooks: ? = to be filled in by Planning SME.

## Forecast Load Energy at Risk
| Project ID | NPR-000771 | NPR-000044 | NPR-000013 | NPR-000805 | NPR-000008 | NPR-000451 | NPR-000060 | NPR-000067 | NPR-000053 | NPR-000070 | NPR-000061 | NPR-000048 | NTM-000009 | NPR-000533 | NPR-000052 | NPR-000049 | NPR-000068
| Asset Name | Third Transformer Eastern Creek ZS | Lowes Creek ZS | West Dapto ZS | North Kemps Creek ZS | Culburra Beach ZS | East Parramatta ZS | Permanent Berrima Junction ZS | Northern Gateway ZS | Austral ZS | Box Hill ZS | Menangle Park ZS | East Riverstone ZS | 132kV Oil Cable Replacement | 132kV Cable Constraints | Cambewarra TS ZS | Mt Gilead ZS | Agribusiness North ZS
| Asset ID | NPR-000771 Augmentation Eastern Creek ZS 3rd Transformer | NPR-000044 Lowes Creek ZS Establishment | NPR-000013 - Establishment of West Dapto ZS | NPR-000805 Establishment of North Kemps Creek ZS | NPR-000008 - Establishment of Culburra Beach ZS | NPR-000451 Augmentation of East Parramatta ZS | NPR-000060 - Permanent Berrima Junction ZS | NPR-000067 Establishment of Northern Gateway ZS | NPR-000053 Establishment of Austral ZS | NPR-000070 Augmentation of Box Hill ZS | NPR-000061 Augmentation of Menangle Park ZS | NPR-000048 Establishment of East Riverstone ZS | Replacement of end of life 132kV oil filled cables in the Parramatta area | 132kV Cable Constaints in the Parramatta area. Augmenting 132kV supply to Parramatta | NPR-000052 Establishment of Cambewarra TS ZS | NPR-000049 Establishment of Mt Gilead ZS | NPR-000068 Establishment of Agribusiness North ZS
Asset Rating (MVA firm) | Year
| 2024 | 45 | 45 | 11.29 | 90 | 4.6 | 90 | 3 | 15 | 50 | 36 | 5.67 | 95 | 0 | 93 | 2.3761 | 7.94 | 0
| 2025 | 45 | 45 | 11.23 | 90 | 4.5 | 90 | 3 | 15 | 50 | 36 | 5.67 | 95 | 0 | 93 | 2.3642 | 7.94 | 0
| 2026 | 45 | 45 | 11.17 | 90 | 4.5 | 90 | 3 | 15 | 50 | 36 | 5.67 | 95 | 0 | 93 | 2.3524 | 7.94 | 0
| 2027 | 45 | 45 | 11.12 | 90 | 4.5 | 90 | 3 | 15 | 50 | 36 | 5.67 | 95 | 0 | 93 | 2.3406 | 7.94 | 0
| 2028 | 45 | 45 | 11.06 | 90 | 4.5 | 90 | 3 | 15 | 50 | 36 | 5.67 | 95 | 0 | 93 | 2.3289 | 7.94 | 0
Asset Rating (MW firm) Formula, assuming a PF | Year
| 2024 | 42.75 | 42.75 | 10.7255 | 89.1 | 4.37 | 85.5 | 2.85 | 14.85 | 49.5 | 34.2 | 5.3865 | 90.25 | 0 | 88.35 | 2.2573 | 7.543 | 0
| 2025 | 42.75 | 42.75 | 10.6685 | 89.1 | 4.275 | 85.5 | 2.85 | 14.85 | 49.5 | 34.2 | 5.3865 | 90.25 | 0 | 88.35 | 2.246 | 7.543 | 0
| 2026 | 42.75 | 42.75 | 10.6115 | 89.1 | 4.275 | 85.5 | 2.85 | 14.85 | 49.5 | 34.2 | 5.3865 | 90.25 | 0 | 88.35 | 2.2347 | 7.543 | 0
| 2027 | 42.75 | 42.75 | 10.564 | 89.1 | 4.275 | 85.5 | 2.85 | 14.85 | 49.5 | 34.2 | 5.3865 | 90.25 | 0 | 88.35 | 2.2236 | 7.543 | 0
| 2028 | 42.75 | 42.75 | 10.507 | 89.1 | 4.275 | 85.5 | 2.85 | 14.85 | 49.5 | 34.2 | 5.3865 | 90.25 | 0 | 88.35 | 2.2124 | 7.543 | 0
Forecast Demand 50% POE (MVA) | Year
| 2024 | 56.5 | 46 | 8.2419 | 69.2 | 5.1005 | 71.5729 | 6.2981 | 17.12 | 53 | 17.3834 | 5.98 | 74.5 | 0 | 72 | 0.658 | 2.86 | 0
| 2025 | 58.1 | 51.7 | 9.0879 | 78.4 | 5.2396 | 78.4335 | 9.0816 | 23.76 | 59.8 | 25.891 | 8.62 | 91.1 | 0 | 72 | 1.222 | 4.16 | 0
| 2026 | 59 | 57.1 | 9.9339 | 88.7 | 5.3299 | 81.3608 | 11.8651 | 29.01 | 67.8 | 30.495 | 10.84 | 101.6 | 0 | 71 | 1.974 | 5.46 | 0
| 2027 | 59.1 | 63.8 | 10.8739 | 98.9 | 5.4201 | 97.0777 | 14.6486 | 21.05 | 76.2 | 36.4736 | 13.7 | 112.2 | 0 | 77 | 2.726 | 7.35 | 0
| 2028 | 59.9 | 70.2 | 11.8139 | 113.4 | 5.4991 | 106.9142 | 15.0331 | 25.02 | 82.2 | 43.7278 | 17.49 | 122.4 | 0 | 82 | 3.478 | 10.74 | 0
Forecast Demand 50% POE (MW) Formula, assuming a PF | Year
| 2024 | 53.675 | 43.7 | 7.8298 | 68.508 | 4.8455 | 67.9943 | 5.9832 | 16.9488 | 52.47 | 16.5142 | 5.681 | 70.775 | 0 | 68.4 | 0.6251 | 2.717 | 0
| 2025 | 55.195 | 49.115 | 8.6335 | 77.616 | 4.9776 | 74.5119 | 8.6275 | 23.5224 | 59.202 | 24.5965 | 8.189 | 86.545 | 0 | 68.4 | 1.1609 | 3.952 | 0
| 2026 | 56.05 | 54.245 | 9.4372 | 87.813 | 5.0634 | 77.2928 | 11.2719 | 28.7199 | 67.122 | 28.9703 | 10.298 | 96.52 | 0 | 67.45 | 1.8753 | 5.187 | 0
| 2027 | 56.145 | 60.61 | 10.3302 | 97.911 | 5.1491 | 92.2238 | 13.9162 | 20.8395 | 75.438 | 34.65 | 13.015 | 106.59 | 0 | 73.15 | 2.5897 | 6.9825 | 0
| 2028 | 56.905 | 66.69 | 11.2232 | 112.266 | 5.2241 | 101.5685 | 14.2815 | 24.7698 | 81.378 | 41.5414 | 16.6155 | 116.28 | 0 | 77.9 | 3.3041 | 10.203 | 0
Forecast Demand 10% POE (MVA) | Year
| 2024 | 56.5 | 46 | 8.2419 | 69.2 | 5.1005 | 74.3729 | 6.2981 | 69.2 | 53 | 17.3834 | 5.98 | 79.3 | 0 | 72 | 0.658 | 2.86 | 0
| 2025 | 58.1 | 51.7 | 9.0879 | 78.4 | 5.2396 | 81.2335 | 9.8736 | 78.4 | 59.8 | 25.891 | 8.62 | 95.9 | 0 | 72 | 1.222 | 4.16 | 0
| 2026 | 59 | 57.1 | 9.9339 | 88.7 | 5.3299 | 84.1608 | 13.4491 | 88.7 | 67.8 | 30.495 | 10.84 | 106.4 | 0 | 71 | 1.974 | 5.46 | 0
| 2027 | 59.1 | 63.8 | 10.8739 | 98.9 | 5.4201 | 99.8777 | 17.0246 | 98.9 | 76.2 | 36.4736 | 13.7 | 117 | 0 | 77 | 2.726 | 7.35 | 0
| 2028 | 59.9 | 70.2 | 11.8139 | 113.4 | 5.4991 | 109.7142 | 18.2011 | 113.4 | 82.2 | 43.7278 | 17.49 | 127.2 | 0 | 82 | 3.478 | 10.74 | 0
Forecast Demand 10% POE (MW) Formula | Year
| 2024 | 53.675 | 43.7 | 7.8298 | 68.508 | 4.8455 | 70.6543 | 5.9832 | 16.9488 | 52.47 | 16.5142 | 5.681 | 75.335 | 0 | 68.4 | 0.6251 | 2.717 | 0
| 2025 | 55.195 | 49.115 | 8.6335 | 77.616 | 4.9776 | 77.1719 | 9.3799 | 23.5224 | 59.202 | 24.5965 | 8.189 | 91.105 | 0 | 68.4 | 1.1609 | 3.952 | 0
| 2026 | 56.05 | 54.245 | 9.4372 | 87.813 | 5.0634 | 79.9528 | 12.7767 | 28.7199 | 67.122 | 28.9703 | 10.298 | 101.08 | 0 | 67.45 | 1.8753 | 5.187 | 0
| 2027 | 56.145 | 60.61 | 10.3302 | 97.911 | 5.1491 | 94.8838 | 16.1734 | 20.8395 | 75.438 | 34.65 | 13.015 | 111.15 | 0 | 73.15 | 2.5897 | 6.9825 | 0
| 2028 | 56.905 | 66.69 | 11.2232 | 112.266 | 5.2241 | 104.2285 | 17.2911 | 24.7698 | 81.378 | 41.5414 | 16.6155 | 120.84 | 0 | 77.9 | 3.3041 | 10.203 | 0
Maximum Load at risk (MW) Formula | Year
| 2024 | 10.925 | 0.95 | 0 | 0 | 0.47548 | 0 | 3.1332 | 2.0988 | 2.97 | 0 | 0.2945 | 0 | 0 | 0 | 0 | -4.826 | 0
| 2025 | 12.445 | 6.365 | 0 | 0 | 0.70264 | 0 | 6.5299 | 8.6724 | 9.702 | 0 | 2.8025 | 0.855 | 0 | 0 | 0 | -3.591 | 0
| 2026 | 13.3 | 11.495 | 0 | 0 | 0.78837 | 0 | 9.9267 | 13.8699 | 17.622 | 0 | 4.9115 | 10.83 | 0 | 0 | 0 | -2.356 | 0
| 2027 | 13.395 | 17.86 | 0 | 8.811 | 0.87409 | 6.7238 | 13.3234 | 5.9895 | 25.938 | 0.44996 | 7.6285 | 20.9 | 0 | 0 | 0 | -0.5605 | 0
| 2028 | 14.155 | 23.94 | 0.71622 | 23.166 | 0.94911 | 16.0685 | 14.4411 | 9.9198 | 31.878 | 7.3414 | 11.229 | 30.59 | 0 | 0 | 1.0917 | 2.66 | 0
Expected Unserved Energy (MWh) | Year
| 2024 | 1 | 0.0046 | 0 | 0 | 0.59844 | 0 | 18.7498 | 0 | 0 | 0 | 0.0022 | 0 | 0 | 0.0076363 | 0 | 0 | 0
| 2025 | 1 | 0.3343 | 0 | 0 | 0.94743 | 0 | 53.4058 | 10.5 | 0.6 | 0 | 0.2907 | 1 | 0 | 0.0076363 | 0 | 0 | 0
| 2026 | 1 | 1.1391 | 0.92075 | 0 | 1.224 | 0 | 88.0644 | 53 | 3.1 | 0 | 1.2794 | 4 | 0 | 0.0010986 | 0 | 0 | 0
| 2027 | 1 | 2.8437 | 8.8669 | 0.2166 | 1.613 | 0.44609 | 122.7216 | 1.9 | 8.8 | 0.00073412 | 4.1458 | 11 | 0 | 0.29818 | 2.0199 | 0 | 0
| 2028 | 1 | 5.4578 | 30.1745 | 9.9733 | 2.0415 | 4.92 | 127.759 | 18.1 | 35.5 | 0.26938 | 42.665 | 23 | 0 | 1.3686 | 31.3193 | 8.9674 | 0